### 场景 1：泄爆分析

建设目标
实现泄爆事故一键触发全维度分析，自动完成多源数据归集与根因溯源，输出符合厂内模板的标准化分析结论；将单起事故分析的数据归集，根因覆盖事故分析。

核心功能

- 一键触发：在 AI 问答界面设置独立「泄爆分析」功能入口，锅炉专工需选定泄爆管段位置（如 #1 炉后屏过热器第 8 屏左数第 3 根）、输入事故发生时间。（可上传泄爆管段图片）

- 系统对图片内容进行精确的缺陷识别，自动结合该管段 超温、金属监督、缺陷管理、检修台账四大业务数据库，拉取事故前3天的全维度关联数据：

- 运行参数类自动提取锅炉负荷曲线、主再热汽温汽压波动、燃料量变化、吹灰器投运时序、烟温偏差、氧量分布等时序数据，自动标记异常波动节点；

- 设备状态类自动调取对应区域阀门动作记录、燃烧器配风历史、支吊架巡检异常记录；

- 历史事件类自动汇总同管排超温时长峰值、历史泄爆档案、遗留缺陷整改进度；

- 检修数据类自动匹配对应管段近 3 次检修的测厚记录、焊口无损检测报告、缺陷处置记录。

- 全程无需人工跨系统导出、整理、比对数据。

- 分层级溯源：模拟资深防磨防爆专家的推理逻辑，按照 “直接爆口原因 - 中期劣化因素 - 底层根因” 三层逻辑开展溯源，从超温热应力损伤、飞灰冲刷磨损、烟气 / 水汽侧腐蚀、焊接与材质原始缺陷、运行操作偏差五大类方向逐项验证。

- 例如针对爆口呈厚唇状特征，自动匹配长期超温蠕变特征，联动对应管段历史超温数据与壁厚减薄趋势交叉验证，最终按影响贡献度输出根因优先级排序，规避单一经验判断的主观偏差，同时为年轻专工标注每一项根因的判定依据与数据支撑。

- 联动案例：分析结果同位置、同类型的历史事故案例、同类型机组典型故障处理经验、对应标准规程条文、防控技术资料，自动推送 “同类爆管预防措施”“同区域改造案例” 等延伸问题，形成 “事故分析 - 知识查阅 - 案例参考 - 能力提升” 的完整闭环。

- 数据依据：

- 管段基础参数：规格材质、壁厚限值、胀粗率限值、壁温限值、累计运行时长。

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- adp.piperow_name AS 管排名称,

- adp.model AS 规格材质,

- adp.piperow_thickness AS 设计壁厚,

- onc.wall_thickness_limit AS 壁厚限值,

- onc.out_thickness_limit AS 胀粗限值,

- btd.over_hot_limit AS 壁温限值,

- RUN_DATA.累计运行时长小时

- FROM

- account_boiler ab

- INNER JOIN account_static_device asd ON ab.boiler_id = asd.boiler_id

- LEFT JOIN account_device_piperow adp ON asd.device_id = adp.device_id

- LEFT JOIN overhaul_new_checklocation onc ON adp.device_id = onc.device_id

- LEFT JOIN base_temp_device btd ON adp.device_id = btd.device_id

- LEFT JOIN (

- SELECT

- boiler_id,

- ROUND( SUM( TIMESTAMPDIFF( SECOND, start_date, stop_date )) / 3600, 2 ) AS 累计运行时长小时

- FROM

- monitor_boiler_start_stop

- GROUP BY

- boiler_id

- ) RUN_DATA ON ab.boiler_id = RUN_DATA.boiler_id -- 组合查询条件

- WHERE

- ab.boiler_name = '1号锅炉'

- AND asd.device_name = '水冷壁螺旋段后墙'

- ORDER BY

- adp.piperow_name;

- 检修处置历史：近 3 次壁厚记录、遗留问题处置结果、年平均减薄速率、泄爆记录、补焊记录、同区域过往换管。

- 近 3 次壁厚记录sql:

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- ob.overhaul_name AS 检修名称,

- ob.begin_date AS 检修时间,

- orc.row_num AS 管排号,

- ort.thickness AS 实测壁厚,

- onc.wall_thickness AS 原始壁厚,

- onc.wall_thickness_limit AS 壁厚限值,

- ort.create_time AS 测量时间

- FROM overhaul_boiler ob

- LEFT JOIN overhaul_record orc ON ob.overhaul_id = orc.overhaul_id

- LEFT JOIN overhaul_record_tubes ort ON orc.id = ort.overhaul_record_id

- LEFT JOIN overhaul_new_checklocation onc ON orc.check_id = onc.id

- LEFT JOIN account_boiler ab ON ob.boiler_id = ab.boiler_id

- LEFT JOIN account_static_device asd ON orc.device_id = asd.device_id

- -- 仅筛选测厚记录

- WHERE orc.mark_type = '1'

- AND ab.boiler_name = '1号锅炉'

- -- AND asd.device_name = '一级省煤器'

- ORDER BY ort.create_time DESC

- LIMIT 3; -- 取最近3条壁厚记录

- 年平均减薄速率sql;

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- ob.overhaul_name AS 检修名称,

- onc.name AS 检测位置名称,

- otr.row_num AS 管排号,

- otr.pipe_num AS 管编号,

- otr.wall_thickness AS 原始壁厚,

- otr.wall_thickness_measure AS 实测壁厚,

- otr.wall_thickness_rate AS 年平均减薄速率,

- otr.out_thickness_rate AS 年胀粗速率,

- otr.residual_life AS 预估剩余寿命,

- otr.last_measure_date AS 末次测量时间

- FROM overhaul_boiler ob

- LEFT JOIN account_boiler ab ON ob.boiler_id = ab.boiler_id

- LEFT JOIN overhaul_thickness_rate otr ON ob.overhaul_id = otr.overhaul_id

- -- 关联检测位置（速率表通过 location_id 关联位置表）

- LEFT JOIN overhaul_new_checklocation onc ON otr.location_id = onc.id

- LEFT JOIN account_static_device asd ON otr.device_id = asd.device_id

- WHERE ab.boiler_name = '1号锅炉'

- -- AND asd.device_name = '一级省煤器'

- ORDER BY otr.row_num, otr.pipe_num;

- 泄爆记录sql:

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- ob.overhaul_name AS 对应检修名称,

- ol.leakage_date AS 泄漏时间,

- ol.leakage_descrip AS 泄漏位置,

- ol.row_num AS 管排号,

- ol.pipe_num AS 管编号,

- ol.leakage_reason AS 泄爆原因,

- ol.handling_method AS 处置方式,

- ol.is_abnormal_stop AS 是否造成非停

- -- 主表改为 overhual_leakage

- FROM overhual_leakage ol

- -- 关联检修策划表

- LEFT JOIN overhaul_boiler ob ON ol.overhaul_id = ob.overhaul_id

- -- 关联锅炉基础表

- LEFT JOIN account_boiler ab ON ol.boiler_id = ab.boiler_id

- -- 关联受热面表

- LEFT JOIN account_static_device asd ON ol.device_id = asd.device_id

- -- 查询条件

- WHERE ab.boiler_name = '1号锅炉'

- -- AND asd.device_name = '一级省煤器'

- ORDER BY ol.leakage_date DESC;

- 补焊记录、同区域过往换管sql：

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- ob.overhaul_name AS 检修名称,

- onc.name AS 检测位置名称,

- ort.tube_position AS 管道位置描述,

- orc.row_num AS 管排号,

- ort.thickness AS 缺陷位置壁厚,

- ort.is_change AS 是否换管,

- CASE

- WHEN ort.is_change = 1 THEN '整体换管'

- WHEN orc.mark_type = 2 AND ort.is_change = 0 THEN '缺陷补焊'

- ELSE '无处置'

- END AS 处置类型,

- orc.defect_type AS 缺陷类型,

- ort.create_time AS 处置时间

- FROM overhaul_boiler ob

- LEFT JOIN account_boiler ab ON ob.boiler_id = ab.boiler_id

- LEFT JOIN overhaul_record orc ON ob.overhaul_id = orc.overhaul_id

- LEFT JOIN overhaul_record_tubes ort ON orc.id = ort.overhaul_record_id

- -- 关联检测位置表

- LEFT JOIN overhaul_new_checklocation onc ON orc.check_id = onc.id

- LEFT JOIN account_static_device asd ON orc.device_id = asd.device_id

- -- 筛选换管/补焊数据

- WHERE (ort.is_change = 1 OR orc.mark_type = 2)

- AND ab.boiler_name = '1号锅炉'

- -- AND asd.device_name = '一级省煤器'

- ORDER BY ort.create_time DESC;

- 壁温超温数据：对应管段累计超温时长、超温峰值、壁温偏差。

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- mht.pi_code AS 测点编码,

- mht.limit_temp AS 设计壁温限值_℃,

- MAX(mht.highest_temp) AS 超温峰值_℃,

- -- 壁温偏差 = 最高壁温 - 设计限值

- MAX(mht.highest_temp) - mht.limit_temp AS 最大壁温偏差_℃,

- -- 累计超温时长 秒转小时，保留2位小数

- ROUND(SUM(mht.limit_duration) / 3600, 2) AS 累计超温总时长_小时

- FROM monitor_hotarea_temp mht

- LEFT JOIN account_boiler ab ON mht.boiler_id = ab.boiler_id

- LEFT JOIN account_static_device asd ON mht.device_id = asd.device_id

- WHERE ab.boiler_name = '1号锅炉'

- AND asd.device_name = '水冷壁螺旋段后墙'  -- 开启受热面名称筛选

- GROUP BY ab.boiler_name, asd.device_name, mht.pi_code, mht.limit_temp

- ORDER BY 累计超温总时长_小时 DESC;

- 吹灰运行数据：对应区域吹灰器吹灰频次、吹扫压力、累计吹扫时长。

- SELECT

- ab.boiler_name AS 锅炉名称,

- asd.device_name AS 受热面名称,

- bsb.blower_name AS 吹灰器名称,

- COUNT(msrr.id) AS 吹灰频次,

- ROUND(SUM(msrr.blowing_duration) / 3600, 2) AS 累计吹扫时长_小时,

- '无采集数据' AS 吹扫压力  -- 系统无该字段

- FROM base_soot_blower bsb

- LEFT JOIN monitor_soot_blower_run_record msrr

- ON bsb.blower_id = msrr.blower_id

- LEFT JOIN account_boiler ab

- ON bsb.boiler_id = ab.boiler_id

- LEFT JOIN account_static_device asd

- ON bsb.device_id = asd.device_id

- WHERE ab.boiler_name = '1号锅炉'

- AND asd.device_name = '水冷壁螺旋段后墙'  -- 受热面筛选条件

- GROUP BY ab.boiler_name, asd.device_name, bsb.blower_name

- ORDER BY 吹灰频次 DESC;

- 烟气煤质数据：对应区域烟温 / 烟速 / 飞灰浓度。

- SELECT

- bpi.pi_code AS 测点编码,

- bpi.pi_name_ch AS 测点名称,

- -- 计算测点平均值、峰值

- AVG(CAST(spd.value AS DECIMAL(8,2))) AS 测点平均值,

- MAX(CAST(spd.value AS DECIMAL(8,2))) AS 测点峰值,

- MAX(spd.data_time) AS 最新采集时间

- FROM sis_pi_data spd

- -- 关联测点基础表（通过测点编码匹配）

- LEFT JOIN base_dev_pi_b bpi ON spd.tag = bpi.pi_code

- -- 按【测点名称】筛选，替换为现场实际测点名称即可

- WHERE bpi.pi_name_ch IN ('烟气温度','烟速','飞灰浓度','吹扫压力')

- GROUP BY bpi.pi_code, bpi.pi_name_ch

- ORDER BY 最新采集时间 DESC;

### 场景 2：缺陷识别

建设目标
实现四管典型缺陷照片自动识别与风险定级；用户根据语义描述缺陷图片的管排信息，来定位缺陷位置，并结合锅炉运行参数给出缺陷分析类型判定，最终依据缺陷知识库内容匹配案例综合模型推理能力给出处置方案。

核心功能

- 缺陷精准识别：适配电厂现场作业环境，支持上传缺陷实拍照片，覆盖水冷壁、过热器、再热器、省煤器全受热面典型缺陷，包括飞灰冲刷磨损沟槽、点蚀 / 均匀腐蚀坑、管壁胀粗、轴向 / 周向表面裂纹、焊口夹渣 / 未熔合成型缺陷、防磨瓦脱落 / 歪斜、管间氧化皮堆积等类型，定位缺陷区域位置并完成缺陷类型的精准判定。

- 缺陷处置方案推送：匹配同类型缺陷的历史处置案例，针对不同风险等级缺陷输出可直接落地的现场处置方案：明确运行监护要求与下次检修的复测周期、检测方式；以及打磨补焊、换管、加装防磨护瓦等标准检修工序的工艺要求。

- 数据依据：

- 管段基础参数：规格材质、壁厚限值、胀粗率限值、壁温限值、累计运行时长。

- 检修处置历史：近 3 次壁厚记录、遗留问题处置结果、年平均减薄速率、泄爆记录、补焊记录、同区域过往换管。

- 壁温超温数据：对应管段累计超温时长、超温峰值、壁温偏差。

- 吹灰运行数据：对应区域吹灰器吹灰频次、吹扫压力、累计吹扫时长。

- 烟气煤质数据：对应区域烟温 / 烟速 / 飞灰浓度。

### 场景 3：检修报告审核

建设目标
实现检修报告1-2轮自动化智能初审，自动提炼报告数据核对规程内容，对漏项内容筛选输出，实现报告漏项检测，减少人工核对的工作量。

核心功能

- 初审校验：基于系统已解析落库的 A 修、C 修、临修检修报告（含测厚报告、无损探伤报告、缺陷处理记录等），自动开展两轮标准化审核。

- 第一轮为完整性审核：对照厂内检修规程、专业检修项目清单、防磨防爆必检区域要求，自动扫描必检管排遗漏、测厚点位数量不足、探伤比例不达标、缺陷验收记录空白、附件资料缺失等问题，例如自动核对高温过热器所有屏数是否均有测厚记录、吹灰器对应区域是否单独开展磨损检查；

- 第二轮为合规性审核：自动校验测厚数据、胀粗数值、探伤结果、缺陷处置工艺等内容是否符合行业标准与厂内管理要求，自动识别壁厚低于警戒值、胀粗率超标、探伤不合格未闭环等问题。

- 问题清单输出：逐条输出漏项与不合规问题清单，每条问题明确标注对应标准规程条文、具体整改要求，无需人工检查编制，大幅减轻检修管理人员的审核与督办工作量。

### 场景 4：资料查询

建设目标
1.实现设备图纸参数自然语言快速查询，实现受热面寿命自动量化评估，输出分级管控方案；结合设备健康状态生成差异化检修指导。

核心功能

- 资料检索：支持自然语言方式查询厂内报告，可按报告名称、所属年限进行筛选。

- 例如锅炉专工输入 “2026年的报告”，系统返回报告列表供用户再次追问，筛选最终结果。

- 图纸检索：支持自然语言方式查询锅炉图纸与设备参数，可按部件名称、安装位置、图号等多维度模糊或精准检索。

- 例如锅炉专工输入 “#2 炉分隔屏过热器第 5 屏 材质壁厚”，系统秒级输出对应部件的材质牌号、设计壁厚 / 管径、设计压力、允许最高壁温、焊接工艺要求、原厂图纸编号等核心参数，无需翻阅厚重的竣工图纸册与设备台账。

### 场景5：检修指导

### 建设目标

- 寿命评估：系统直接从台账库提取管段近 3 次的历史测厚数据、累计运行小时数、超温历史总时长与峰值温度，自动计算年减薄速率、剩余有效壁厚、蠕变损伤系数，输出精准的减薄率数值、剩余安全寿命预测结论，配套给出需要进行换管和测量的计划管道详情方案。

- 作业指导：根据用户选定的检修类型（A 修 / C 修 ），联动管段健康数据、超温预警、缺陷分布、寿命评估结果，对照行业防磨防爆检查标准，自动梳理重点检查区域清单与优先级排序，输出分岗位作业要点、检测布点方案、安全作业注意事项。

- 例如针对 C 修场景，系统自动标记上一年度超温频次高的屏区、测厚减薄快的区域、吹灰器正对磨损区为一级必查区域，对应增加测厚点数与探伤比例；对状态良好的区域降低检查频次，实现 “一区一策” 的精准检修指导，替代传统一刀切的固化检修模式，生成的检修项目清单可直接导出补充检修计划。